Project: Goldstone Infratech Ltd. – E-Bus Division

System: 415 V, 3-Phase, 50 Hz     Power Factor: 0.8 Basis: Corrected Cable Sizing Excel Workbook

CABLE SIZING CALCULATION ANNEXURE

Prepared By: _________B. KESHAVARDHAN NAYAK___________     Checked By: ____________________     Approved By: ____________________

Revision: 00     Date: ________11-08-2026____________

# DESIGN BASIS

The annexure follows the parameters and terminology used in the completed cable-sizing workbook.

| Parameter | Design Value |
| --- | --- |
| System voltage | 415 V |
| System | 3-phase AC |
| Power factor | 0.8 |
| Frequency | 50 Hz |
| Conductor | Aluminium |
| Insulation | XLPE |
| Installation methods | Underground / In Air, as stated per feeder |
| Voltage-drop criterion | 3% |
| Load-current formula | I = P / (√3 × V × PF) |

# CALCULATION METHODOLOGY

Full-load current: IFL = P / (√3 × V × PF) Derated current: I	 = IFL / K, where K is the combined rating factor used in the workbook. Derated

Overall CCC: CCC	 = CCC	 × number of parallel runs. Overall, single cable

CCC check: PASS when Overall CCC ≥ Derated Current.

Voltage drop: Vd = √3 × I × L × (R cosφ + X sinφ) / N

For PF = 0.8, cosφ = 0.8 and sinφ = 0.6.

Voltage-drop check: PASS when percentage voltage drop is below 3%,.

# 2.DETAILED MAIN FEEDER CALCULATIONS

The following examples reproduce the calculation basis used for the principal MCC outgoing feeders.

| Item | Result |
| --- | --- |
| Feeder | MCC → Bay -1 |
| Load | 359.00 kW |
| Full-load current | 624.30 A |
| Derating factor K | 0.556920 |
| Derated current | 1120.99 A |
| Selected cable | 400sq.mmALXLPE |
| No. of runs / phase | 5 |
| Cable type | 5Rx1Cx400xALXLPE |
| Laying method | Under Ground |
| CCC / cable | 431 A |
| Overall CCC | 2155 A |
| CCC check | PASS |
| Cable length | 0.22 km |
| R | 0.1000 Ω/km |
| X | 0.0787 Ω/km |
| Running voltage drop | 6.05 V (1.46%) |
| Voltage-drop check | PASS |
| Item | Result |
| Feeder | MCC → Bay -2 |
| Load | 114.00 kW |
| Full-load current | 198.25 A |
| Derating factor K | 0.556920 |
| Derated current | 355.97 A |
| Selected cable | 300sq.mmALXLPE |

| No. of runs / phase | 2 |
| --- | --- |
| Cable type | 2Rx1Cx300xALXLPE |
| Laying method | Under Ground |
| CCC / cable | 376 A |
| Overall CCC | 752 A |
| CCC check | PASS |
| Cable length | 0.22 km |
| R | 0.1280 Ω/km |
| X | 0.0795 Ω/km |
| Running voltage drop | 5.67 V (1.37%) |
| Voltage-drop check | PASS |
| Item | Result |
| Feeder | MCC → Bay -3 |
| Load | 45.00 kW |
| Full-load current | 78.26 A |
| Derating factor K | 0.501228 |
| Derated current | 156.13 A |
| Selected cable | 70sq.mmALXLPE |
| No. of runs / phase | 2 |
| Cable type | 2Rx1Cx70xALXLPE |
| Laying method | Under Ground |
| CCC / cable | 166 A |
| Overall CCC | 332 A |
| CCC check | PASS |
| Cable length | 0.22 km |
| R | 0.5670 Ω/km |
| X | 0.0900 Ω/km |
| Running voltage drop | 7.57 V (1.82%) |

| Voltage-drop check | PASS |
| --- | --- |
| Item | Result |
| Feeder | MCC → Bay - 4 |
| Load | 67.00 kW |
| Full-load current | 116.51 A |
| Derating factor K | 0.501228 |
| Derated current | 232.46 A |
| Selected cable | 70sq.mmALXLPE |
| No. of runs / phase | 3 |
| Cable type | 3Rx1Cx70xALXLPE |
| Laying method | Under Ground |
| CCC / cable | 166 A |
| Overall CCC | 498 A |
| CCC check | PASS |
| Cable length | 0.22 km |
| R | 0.5670 Ω/km |
| X | 0.0900 Ω/km |
| Running voltage drop | 7.51 V (1.81%) |
| Voltage-drop check | PASS |
| Item | Result |
| Feeder | MCC → Utilities |
| Load | 38.00 kW |
| Full-load current | 66.08 A |
| Derating factor K | 0.501228 |
| Derated current | 131.84 A |
| Selected cable | 50sq.mmALXLPE |
| No. of runs / phase | 2 |

| Cable type | 2Rx1Cx50xALXLPE |
| --- | --- |
| Laying method | Under Ground |
| CCC / cable | 135 A |
| Overall CCC | 270 A |
| CCC check | PASS |
| Cable length | 0.22 km |
| R | 0.8200 Ω/km |
| X | 0.0937 Ω/km |
| Running voltage drop | 8.97 V (2.16%) |
| Voltage-drop check | PASS |
| Item | Result |
| Feeder | MCC → Lighting Panel |
| Load | 21.60 kW |
| Full-load current | 37.56 A |
| Derating factor K | 0.501228 |
| Derated current | 74.94 A |
| Selected cable | 16sq.mmALXLPE |
| No. of runs / phase | 3 |
| Cable type | 3Rx1Cx16xALXLPE |
| Laying method | Under Ground |
| CCC / cable | 76 A |
| Overall CCC | 228 A |
| CCC check | PASS |
| Cable length | 0.22 km |
| R | 2.4400 Ω/km |
| X | 0.1080 Ω/km |
| Running voltage drop | 9.62 V (2.32%) |
| Voltage-drop check | PASS |

# COMPLETE FEEDER-WISE CABLE SIZING SUMMARY

Active feeders covered: 156. All active rows in the corrected workbook pass the CCC and running-voltage-drop checks using the workbook's 3% criterion.

| S.N. | From | To | kW | IFL A | K | Ider A | Cable | Runs | CCC A | Overall A | Len km | VD % | CCC | VD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | MCC | Bay -1 | 359.0 | 624.3 | 0.5569 | 1121.0 | 400sq.mm | 5 | 431 | 2155 | 0.22 | 1.46 | PASS | PASS |
| 2 | MCC | Bay -2 | 114.0 | 198.2 | 0.5569 | 356.0 | 300sq.mm | 2 | 376 | 752 | 0.22 | 1.37 | PASS | PASS |
| 3 | MCC | Bay -3 | 45.0 | 78.3 | 0.5012 | 156.1 | 70sq.mm | 2 | 166 | 332 | 0.22 | 1.82 | PASS | PASS |
| 4 | MCC | Bay - 4 | 67.0 | 116.5 | 0.5012 | 232.5 | 70sq.mm | 3 | 166 | 498 | 0.22 | 1.81 | PASS | PASS |
| 5 | MCC | Utilities | 38.0 | 66.1 | 0.5012 | 131.8 | 50sq.mm | 2 | 135 | 270 | 0.22 | 2.16 | PASS | PASS |
| 6 | MCC | Lighting Panel | 21.6 | 37.6 | 0.5012 | 74.9 | 16sq.mm | 3 | 76 | 228 | 0.22 | 2.32 | PASS | PASS |
| 7 | MCC | Capacitor Bank -1 | 500.0 | 869.5 | 0.5569 | 1561.3 | 630sq.mm | 6 | 557 | 3342 | 0.22 | 1.27 | PASS | PASS |
| 8 | MCC | Material Preparation and Workshop | 186.0 | 323.5 | 0.5569 | 580.8 | 240sq.mm | 4 | 332 | 1328 | 0.22 | 1.31 | PASS | PASS |
| 9 | Bay - 1 | Battery Charger -1 | 80.0 | 139.1 | 0.5569 | 249.8 | 50sq.mm | 3 | 150 | 450 | 0.15 | 2.07 | PASS | PASS |
| 10 | Bay -1 | Battery Charger - 2 | 80.0 | 139.1 | 0.5569 | 249.8 | 50sq.mm | 3 | 150 | 450 | 0.15 | 2.07 | PASS | PASS |
| 11 | Bay - 1 | Battery Charger -3 | 80.0 | 139.1 | 0.5569 | 249.8 | 50sq.mm | 3 | 150 | 450 | 0.15 | 2.07 | PASS | PASS |
| 12 | Bay - 1 | Battery Charger -4 | 80.0 | 139.1 | 0.5569 | 249.8 | 50sq.mm | 3 | 150 | 450 | 0.15 | 2.07 | PASS | PASS |
| 13 | Bay - 1 | Welding Machine | 7.5 | 13.0 | 0.7155 | 18.2 | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 14 | Bay - 1 | Welding Machine | 7.5 | 13.0 | 0.7155 | 18.2 | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 15 | Bay - 1 | Welding Machine | 7.5 | 13.0 | 0.7155 | 18.2 | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 16 | Bay - 1 | Welding Machine | 7.5 | 13.0 | 0.7155 | 18.2 | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 17 | Bay - 1 | Welding Machine | 7.5 | 13.0 | 0.7155 | 18.2 | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 18 | Bay - 1 | Welding Machine | 7.5 | 13.0 | 0.7155 | 18.2 | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 19 | Bay - 1 | Welding Machine | 7.5 | 13.0 | 0.7155 | 18.2 | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 20 | Bay - 1 | Welding Machine | 7.5 | 13.0 | 0.7155 | 18.2 | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 21 | Bay - 1 | Welding Machine | 7.5 | 13.0 | 0.7155 | 18.2 | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 22 | Bay - 1 | Welding Machine | 7.5 | 13.0 | 0.7155 | 18.2 | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 23 | Bay - 1 | Welding Machine | 7.5 | 13.0 | 0.7155 | 18.2 | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 24 | Bay - 1 | Welding Machine | 7.5 | 13.0 | 0.7155 | 18.2 | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 25 | Bay - 1 | Grinding Machine | 1.0 | 1.7 | 0.7155 | 2.4 | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |

| S.N. | From | To | kW | IFL A | K |  | Ider A | Cable |  | Runs | CCC A | Overall A | Len km | VD % | CCC | VD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 26 | Bay - 1 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 27 | Bay - 1 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |

| S.N. | From | To | kW | IFL A | K |  | Ider A | Cable |  | Runs | CCC A | Overall A | Len km | VD % | CCC | VD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 28 | Bay - 1 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 29 | Bay - 1 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 30 | Bay - 1 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 31 | Bay - 1 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 32 | Bay - 1 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 33 | Bay - 1 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 34 | Bay - 1 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 35 | Bay - 1 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 36 | Bay - 1 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 37 | Bay - 1 | Blower, Paint Booth | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 38 | Bay - 1 | Blower, Paint Booth | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 39 | Bay - 1 | Blower, Paint Booth | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 40 | Bay - 1 | Blower, Paint Booth | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 41 | Bay - 2 | EOT Crane -1 | 15.0 | 26.1 |  | 0.7155 | 36.5 |  | 10sq.mm | 3 | 53 | 159 | 0.22 | 2.57 | PASS | PASS |
| 42 | Bay- 2 | Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 43 | Bay - 2 | Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 44 | Bay - 2 | Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 45 | Bay- 2 | Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 46 | Bay - 2 | Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 47 | Bay - 2 | Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 48 | Bay- 2 | Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 49 | Bay - 2 | Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 50 | Bay - 2 | Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 51 | Bay - 2 | Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 52 | Bay - 2 | Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 53 | Bay - 2 | Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 54 | Bay - 2 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |

| S.N. | From | To | kW | IFL A | K |  | Ider A | Cable |  | Runs | CCC A | Overall A | Len km | VD % | CCC | VD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 55 | Bay - 2 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 56 | Bay - 2 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 57 | Bay - 2 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 58 | Bay - 2 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 59 | Bay - 2 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 60 | Bay - 2 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 61 | Bay - 2 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 62 | Bay - 2 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 63 | Bay - 2 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 64 | Bay - 2 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 65 | Bay - 2 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 66 | Bay - 2 | Int.Med. Trolley | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 67 | Bay - 2 | Int.Med. Trolley | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 68 | Bay - 2 | Int.Med. Trolley | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 69 | Bay- 2 | Int.Med. Trolley | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 70 | Bay - 2 | Int.Med. Trolley | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 71 | Bay - 2 | Int.Med. Trolley | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 72 | Bay - 2 | Blower, Paint Booth | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 73 | Bay - 2 | Blower, Paint Booth | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 74 | Bay - 2 | Nut Runners | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 75 | Bay - 2 | Nut Runners | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 76 | Bay - 2 | Nut Runners | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 77 | Bay - 2 | Nut Runners | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 78 | Bay - 2 | Pnuematic Chisels | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 79 | Bay - 2 | Pnuematic Chisels | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 85 | Bay - 3 | EOT Crane -1 | 15.0 | 26.1 |  | 0.7155 | 36.5 |  | 10sq.mm | 3 | 53 | 159 | 0.22 | 2.57 | PASS | PASS |
| 86 | Bay - 3 | Vinyl Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |

| S.N. | From | To | kW | IFL A | K |  | Ider A | Cable |  | Runs | CCC A | Overall A | Len km | VD % | CCC | VD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 87 | Bay -3 | Vinyl Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 88 | Bay - 3 | Vinyl Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 89 | Bay - 3 | Vinyl Welding Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 90 | Bay - 3 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 91 | Bay - 3 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 92 | Bay - 3 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 93 | Bay - 3 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 94 | Bay - 3 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 95 | Bay - 3 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 96 | Bay - 3 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 97 | Bay - 3 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 98 | Bay - 3 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 99 | Bay - 3 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 100 | Bay - 3 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 101 | Bay - 3 | Grinding Machine | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 102 | Bay - 3 | Pnuematic Chisels | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 103 | Bay - 3 | Pnuematic Chisels | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 104 | Bay - 3 | Nut Runners | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 105 | Bay - 3 | Nut Runners | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 106 | Bay - 3 | Nut Runners | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 107 | Bay - 3 | Nut Runners | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 108 | Bay - 3 | Blower, Paint Booth | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 109 | Bay - 3 | Blower, Paint Booth | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 110 | Bay - 4 | Brake test | 20.0 | 34.8 |  | 0.7155 | 48.6 |  | 16sq.mm | 3 | 73 | 219 | 0.22 | 2.15 | PASS | PASS |
| 111 | Bay - 4 | SideSlip test | 3.0 | 5.2 |  | 0.7155 | 7.3 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.83 | PASS | PASS |
| 112 | Bay - 4 | Wheel Alignment | 2.0 | 3.5 |  | 0.7155 | 4.9 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.56 | PASS | PASS |
| 113 | Bay - 4 | Sleep test | 3.0 | 5.2 |  | 0.7155 | 7.3 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.83 | PASS | PASS |

| S.N. | From | To | kW | IFL A | K |  | Ider A | Cable |  | Runs | CCC A | Overall A | Len km | VD % | CCC | VD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 114 | Bay - 4 | Plug & Socket | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 115 | Bay - 4 | Plug & Socket | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 116 | Bay - 4 | Plug & Socket | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 117 | Bay - 4 | Plug & Socket | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 118 | Bay - 4 | Plug & Socket | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 119 | Bay - 4 | Plug & Socket | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 120 | Bay - 4 | Plug & Socket | 3.0 | 5.2 |  | 0.7155 | 7.3 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.83 | PASS | PASS |
| 121 | Bay - 4 | Plug & Socket | 3.0 | 5.2 |  | 0.7155 | 7.3 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.83 | PASS | PASS |
| 122 | Bay - 4 | Plug & Socket | 3.0 | 5.2 |  | 0.7155 | 7.3 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.83 | PASS | PASS |
| 123 | Bay - 4 | Plug & Socket | 3.0 | 5.2 |  | 0.7155 | 7.3 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.83 | PASS | PASS |
| 124 | Bay - 4 | Plug & Socket | 3.0 | 5.2 |  | 0.7155 | 7.3 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.83 | PASS | PASS |
| 125 | Lighting Panel | LDB | 21.6 | 37.6 |  | 0.7155 | 52.5 |  | 10sq.mm | 3 | 53 | 159 | 0.15 | 2.52 | PASS | PASS |
| 127 | Capacitor Panel | Capacitor Bank | 10.0 | 17.4 |  | 0.7155 | 24.3 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.78 | PASS | PASS |
| 128 | Capacitor Panel | Capacitor Bank | 20.0 | 34.8 |  | 0.7155 | 48.6 |  | 10sq.mm | 3 | 53 | 159 | 0.15 | 2.34 | PASS | PASS |
| 129 | Capacitor Panel | Capacitor Bank | 20.0 | 34.8 |  | 0.7155 | 48.6 |  | 10sq.mm | 3 | 53 | 159 | 0.15 | 2.34 | PASS | PASS |
| 130 | Capacitor Panel | Capacitor Bank | 100.0 | 173.9 |  | 0.7155 | 243.1 |  | 50sq.mm | 3 | 150 | 450 | 0.15 | 2.58 | PASS | PASS |
| 131 | Capacitor Panel | Capacitor Bank | 50.0 | 87.0 |  | 0.7155 | 121.5 |  | 25sq.mm | 3 | 98 | 294 | 0.15 | 2.35 | PASS | PASS |
| 132 | Capacitor Panel | Capacitor Bank | 50.0 | 87.0 |  | 0.7155 | 121.5 |  | 25sq.mm | 3 | 98 | 294 | 0.15 | 2.35 | PASS | PASS |
| 133 | Capacitor Panel | Capacitor Bank | 50.0 | 87.0 |  | 0.7155 | 121.5 |  | 25sq.mm | 3 | 98 | 294 | 0.15 | 2.35 | PASS | PASS |
| 134 | Capacitor Panel | Capacitor Bank | 50.0 | 87.0 |  | 0.7155 | 121.5 |  | 25sq.mm | 3 | 98 | 294 | 0.15 | 2.35 | PASS | PASS |
| 135 | Capacitor Panel | Capacitor Bank | 50.0 | 87.0 |  | 0.7155 | 121.5 |  | 25sq.mm | 3 | 98 | 294 | 0.15 | 2.35 | PASS | PASS |
| 136 | Capacitor Panel | Capacitor Bank | 25.0 | 43.5 |  | 0.7155 | 60.8 |  | 10sq.mm | 3 | 53 | 159 | 0.15 | 2.92 | PASS | PASS |
| 137 | Capacitor Panel | Capacitor Bank | 25.0 | 43.5 |  | 0.7155 | 60.8 |  | 10sq.mm | 3 | 53 | 159 | 0.15 | 2.92 | PASS | PASS |
| 138 | Capacitor Panel | Capacitor Bank | 25.0 | 43.5 |  | 0.7155 | 60.8 |  | 10sq.mm | 3 | 53 | 159 | 0.15 | 2.92 | PASS | PASS |
| 139 | Capacitor Panel | Capacitor Bank | 25.0 | 43.5 |  | 0.7155 | 60.8 |  | 10sq.mm | 3 | 53 | 159 | 0.15 | 2.92 | PASS | PASS |
| 140 | MP&WP | Press Break | 25.0 | 43.5 |  | 0.7155 | 60.8 |  | 10sq.mm | 3 | 53 | 159 | 0.15 | 2.92 | PASS | PASS |
| 141 | MP&WP | Press Break | 25.0 | 43.5 |  | 0.7155 | 60.8 |  | 10sq.mm | 3 | 53 | 159 | 0.15 | 2.92 | PASS | PASS |

| S.N. | From | To | kW | IFL A | K |  | Ider A | Cable |  | Runs | CCC A | Overall A | Len km | VD % | CCC | VD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 142 | MP&WP | Shearing Machine- 1 | 15.0 | 26.1 |  | 0.7155 | 36.5 |  | 6sq.mm | 3 | 39 | 117 | 0.15 | 2.61 | PASS | PASS |
| 143 | MP&WP | Shearing Machine- 2 | 15.0 | 26.1 |  | 0.7155 | 36.5 |  | 6sq.mm | 3 | 39 | 117 | 0.15 | 2.61 | PASS | PASS |
| 144 | MP&WP | Section Bending | 1.0 | 1.7 |  | 0.7155 | 2.4 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.28 | PASS | PASS |
| 145 | MP&WP | Band Saw -1 | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 146 | MP&WP | Band Saw -2 | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 147 | MP&WP | Band Saw -3 | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 148 | MP&WP | Iron Worker | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 149 | MP&WP | Burr Remover | 2.0 | 3.5 |  | 0.7155 | 4.9 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.56 | PASS | PASS |
| 150 | MP&WP | Burr Remover | 2.0 | 3.5 |  | 0.7155 | 4.9 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.56 | PASS | PASS |
| 151 | MP&WP | Straining Machine -1 | 3.0 | 5.2 |  | 0.7155 | 7.3 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.83 | PASS | PASS |
| 152 | MP&WP | Straining Machine -2 | 3.0 | 5.2 |  | 0.7155 | 7.3 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 0.83 | PASS | PASS |
| 153 | MP&WP | Wood Cutting - 1 | 5.0 | 8.7 |  | 0.7155 | 12.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 1.39 | PASS | PASS |
| 154 | MP&WP | Wood Cutting - 2 | 5.0 | 8.7 |  | 0.7155 | 12.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 1.39 | PASS | PASS |
| 155 | MP&WP | Hydraulic Press | 15.0 | 26.1 |  | 0.7155 | 36.5 |  | 6sq.mm | 3 | 39 | 117 | 0.15 | 2.61 | PASS | PASS |
| 156 | MP&WP | Hydraulic Press | 15.0 | 26.1 |  | 0.7155 | 36.5 |  | 6sq.mm | 3 | 39 | 117 | 0.15 | 2.61 | PASS | PASS |
| 157 | MP&WP | Profile Laser Machine | 10.0 | 17.4 |  | 0.7155 | 24.3 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.78 | PASS | PASS |
| 158 | MP&WP | Radial Drill Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 159 | MP&WP | Drilling Machine | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |
| 160 | Utilities | BoreWell | 15.0 | 26.1 |  | 0.7155 | 36.5 |  | 6sq.mm | 3 | 39 | 117 | 0.15 | 2.61 | PASS | PASS |
| 161 | Utilities | Pump | 15.0 | 26.1 |  | 0.7155 | 36.5 |  | 6sq.mm | 3 | 39 | 117 | 0.15 | 2.61 | PASS | PASS |
| 162 | Utilities | ETP & Sludge Pit | 7.5 | 13.0 |  | 0.7155 | 18.2 |  | 4sq.mm | 3 | 31 | 93 | 0.15 | 2.09 | PASS | PASS |

# SUMMARY OF CABLE LENGTHS

The cable-length summary below is reproduced from the corrected workbook's summary section. Total cable length is the sum of route length multiplied by the number of parallel runs.

| Cable Size | Total Length (km) | Total Length (m) |
| --- | --- | --- |
| 4 sq.mm Al XLPE | 54.00 | 54,000 |
| 6 sq.mm Al XLPE | 2.70 | 2,700 |
| 10 sq.mm Al XLPE | 5.37 | 5,370 |
| 16 sq.mm Al XLPE | 1.32 | 1,320 |
| 25 sq.mm Al XLPE | 2.25 | 2,250 |
| 50 sq.mm Al XLPE | 2.69 | 2,690 |
| 70 sq.mm Al XLPE | 1.10 | 1,100 |
| 240 sq.mm Al XLPE | 0.88 | 880 |
| 300 sq.mm Al XLPE | 0.44 | 440 |
| 400 sq.mm Al XLPE | 1.10 | 1,100 |
| 630 sq.mm Al XLPE | 1.32 | 1,320 |
| GRAND TOTAL | 73.17 | 73,170 |

# DOCUMENT CONTROL

Prepared By: ________________________________

Checked By: _________________________________

Approved By: _________________________________ Revision: 00     Date: ____________________

Reference: Completed cable-sizing workbook and supplied LT XLPE cable catalogue. Cable resistance/reactance and current ratings are taken from the supplied cable data used in the workbook.