Project: Goldstone Infratech Ltd. – E-Bus Division

System: 415 V, 3-Phase, 50 Hz

Power Factor: 0.8

CABLE SIZING EXPLANATION DOCUMENT

RUNNING VOLTAGE DROP CALCULATION

# DOCUMENT CONTROL / APPROVAL

Prepared By: ____B.KESHAVARDHAN NAYAK________________ Checked By: ____________________ Approved By: ____________________

# 1. PURPOSE AND SCOPE

This document explains the running voltage-drop calculation used in the completed cable-sizing workbook. The calculation is used to verify that the selected cable size and number of parallel runs maintain the feeder voltage drop within the project criterion.

# 2. DESIGN PARAMETERS

| Parameter | Value |
| --- | --- |
| System Voltage | 415 V |
| System | 3-Phase AC |
| Frequency | 50 Hz |
| Power Factor | 0.8 |
| Conductor | Aluminium |
| Insulation | XLPE |
| Voltage Drop Criterion | 3% |

# 3. FULL-LOAD CURRENT

For a three-phase load, the full-load current is calculated using the following formula:

I_FL = P / (√3 × V × PF)

Where P is the connected load in watts, V is the line-to-line system voltage in volts, and PF is the power factor.

For the project calculations, the system voltage is 415 V and the power factor used is 0.8.

# 4. DERATING FACTOR

The cable current-carrying capacity is affected by the installation conditions. The applicable combined rating factor K is used to determine the derated design current.

I_derated = I_FL / K

The selected cable arrangement must provide sufficient current-carrying capacity after the applicable derating factor is applied.

# 5. CABLE SIZE AND NUMBER OF RUNS

The cable size is selected from the applicable aluminium XLPE cable data. When one cable is insufficient for the required current, parallel cable runs are considered.

Overall CCC = CCC of one cable × Number of Parallel Runs

The current-carrying-capacity check is satisfied when the overall available CCC is greater than or equal to the derated design current.

# 6. RUNNING VOLTAGE DROP

Running voltage drop is calculated using the feeder current, cable length, cable resistance, cable reactance, power factor and number of parallel runs.

V_D = √3 × I × L × (R cosφ + X sinφ) / N

Where:

I = running current in amperes

L = cable route length in kilometres

R = cable resistance in Ω/km

X = cable reactance in Ω/km

φ = power-factor angle

N = number of parallel cable runs

# 7. POWER FACTOR COMPONENTS

For the project power factor of 0.8:

cosφ = 0.8

sinφ = √(1 − 0.8²) = 0.6

# 8. RUNNING VOLTAGE DROP PERCENTAGE

The voltage-drop percentage is calculated with respect to the 415 V system voltage:

VD% = (V_D / 415) × 100

The completed workbook uses a 3% running-voltage-drop criterion. Therefore, the feeder is considered to pass the running voltage-drop check when the calculated percentage is below 3%.

# 9. EXAMPLE CALCULATION

Example values are shown below to demonstrate the calculation method. Actual feeder values must be taken from the completed workbook.

| Parameter | Example Value |
| --- | --- |
| Running current | 624.3 A |
| Cable length | 0.220 km |
| Power factor | 0.8 |
| cosφ | 0.8 |
| sinφ | 0.6 |
| R | 0.547 Ω/km |
| X | 0.0740 Ω/km |
| Number of runs | 2 |
| System voltage | 415 V |

V_D = √3 × 624.3 × 0.220 × (0.547 × 0.8 + 0.0740 × 0.6) / 2

V_D ≈ 90.2 V

VD% ≈ 21.7%

This example is illustrative only and is not a final feeder result. The actual calculation must use the final cable R, X, length, current and number of runs from the approved workbook.

# 10. RUNNING VOLTAGE DROP CHECK

| Check | Requirement | Result |
| --- | --- | --- |
| Running Voltage Drop | VD% < 3% | PASS / FAIL |
| Cable CCC | Overall CCC ≥ Derated Current | PASS / FAIL |

# 11. CABLE RESISTANCE AND REACTANCE

The R and X values used in the running voltage-drop calculation must correspond to the selected cable size and cable construction. The supplied LT XLPE cable catalogue provides resistance and approximate reactance data for the applicable aluminium XLPE cables.

# 12. CABLE LENGTH CALCULATION

After selecting the cable size and number of runs, the total cable quantity is calculated as:

Total Cable Length = Route Length per Run × Number of Parallel Runs

Example: 0.220 km route × 2 runs = 0.440 km total cable.

# 13. FINAL RUNNING VOLTAGE-DROP WORKFLOW

Load → Full-Load Current → Derating → Cable Size → Number of Runs → R/X Values → Running Voltage Drop → Voltage Drop Percentage → 3% Check → Final Cable Selection

# 14. CONCLUSION

The running voltage-drop calculation verifies the voltage performance of the selected feeder cable arrangement. The final cable arrangement is accepted only when the calculated running voltage drop satisfies the applicable project criterion and the cable current-carrying capacity is adequate.